## Slide 1: Section 5: Modeling Population Variability
Problem: what to do when information cannot be pooled
  Across components
  Across plants
  Across time
  Across experts
Inappropriately pooling information leads to underestimation of uncertainty

## Slide 2: Variability Model Options
Pool | Pool | Population Variability
Xn | Plant Specific Xp np | Population Model Xi + ni
λLOSP | λLOSPplant | λLOSPi
Notes: Because of partial pooling of data in this approach, the effective number of parameters is between 2 and n + 2. Use of DIC for model selection is based on choosing the model with the fewest effective parameters.

## Slide 3: Example: Variability in LOSP
Xi is number of LOSP events at Plant i in time ti
Assume variability in LOSP from plant to plant can be modeled with a gamma distribution
  LOSP, i ~ gamma(, ) , i = 1, 2, …, n
There are (n + 2) unknown parameters: LOSP, i, , 
In past problems we specified  and , and there was only one LOSP
   and  are now uncertain
Notes: Because of partial pooling of data in this approach, the effective number of parameters is between 2 and n + 2. Use of DIC for model selection is based on choosing the model with the fewest effective parameters.

## Slide 4: DAG Model
alpha
beta
lambda.losp[i]
Time[i]
mean[i]
X[i]
for(i in 1:N)
Notes: Note that the lambda’s are conditionally independent, given alpha and beta.
Requires assumption that x’s are exchangeable. If there is reason to believe, a priori, that a particular plant is better or worse than others, then this assumption does not hold. This can also be a crucial assumption when looking at year-to-year variability.

## Slide 5: Another Representation of the Problem

## Slide 6: Hierarchical Bayes
Previous approach is called “hierarchical Bayes”
  Bayesian approach is to specify prior in stages (hierarchies)
    First stage is gamma(, ) prior for LOSP, i
      Also known as the Population Variability Curve (PVC)
    Second stage is joint prior o(, )
      Called hyperprior
      ,  called hyperparameters
      Often use vague (noninformative) prior for hyperparameters
    Two stages typical, but can model three or more
Overall prior
First-stage prior
Second-stage prior (hyperprior)

## Slide 7: Example: Variability in LOSP Frequency
Data
Plant | Failures | Time (yrs)
Plant 1 | 2 | 15.986
Plant 2 | 1 | 16.878
Plant 3 | 1 | 18.146
Plant 4 | 1 | 18.636
Plant 5 | 2 | 18.792
Plant 6 | 0 | 18.976
Plant 7 | 12 | 18.522
Plant 8 | 5 | 19.04
Plant 9 | 0 | 18.784
Plant 10 | 3 | 18.868
Plant 11 | 0 | 19.232

## Slide 8: OpenBUGS Model
Hierarchical LOSP frequency.odc
model {
for (i in 1 : N) {
lambda.losp[i] ~ dgamma(alpha, beta) #Model variability in LOSP frequency (PVC)
mean[i] <- lambda.losp[i] * time[i] #Poisson parameter for each plant
x[i] ~ dpois(mean[i]) #Poisson distribution for events at each plant
}
lambda.ind ~ dgamma(alpha, beta)
alpha ~ dgamma(0.0001, 0.0001) #Vague hyperprior for alpha
beta ~ dgamma(0.0001, 0.0001) #Vague hyperprior for beta
}
data
Use data from LOSP frequencies.txt
inits
list(alpha=1, beta=1)
list(alpha=0.5, beta=5)
Notes: Be sure to point out need to check carefully for convergence.

## Slide 9: Results

## Slide 10: Results

## Slide 11: Exercises
Analyze the pooled data using the Jeffreys prior and compare the results to those from the hierarchical model.
Replace the gamma first-stage prior with a lognormal distribution. Use a dflat() hyperprior for the first parameter. For the second parameter, reparameterize in terms of  and place a dunif(0, 10) hyperprior on .
  How do the mean and median of lambda.ind compare to the previous results? Explain.
  How do the 90% intervals compare.
  Any conclusions about choosing a first-stage prior?
Notes: If class is fairly advanced, instructor can illustrate predicted event count under the pooled-data model as another lead-in to model checking.

## Slide 12: Example: Variability in EDG FTS Probability
Assume Xi ~ binomial(pFTS, i, ni) for each EDG
Assume pFTS, i ~ beta(, )
Assume  and  have independent, vague hyperpriors
  o(, ) = o()o()
  Vague hyperprior is gamma with both
  parameters << 1

## Slide 13: Variability in EDG FTS Probability (cont.)
Data
Data taken from
(Siu and Kelly, 1998)
 | Failures | Demands
Plant 1 | 0 | 140
Plant 2 | 0 | 130
Plant 3 | 0 | 130
Plant 4 | 1 | 130
Plant 5 | 2 | 100
Plant 6 | 3 | 185
Plant 7 | 3 | 175
Plant 8 | 4 | 167
Plant 9 | 5 | 151
Plant 10 | 10 | 150

## Slide 14: DAG Model

## Slide 15: OpenBUGS Model
hierarchical EDG FTS probability.odc
model {
for (i in 1 : N) {
x[i] ~ dbin(p.fts[i], n[i]) #Binomial distribution for EDG failures
p.fts[i] ~ dbeta(alpha, beta) #Beta prior for FTS probability
}
p.ind ~ dbeta(alpha, beta)
alpha ~ dgamma(0.0001, 0.0001) #Vague hyperprior for alpha
beta ~ dgamma(0.0001, 0.0001) #Vague hyperprior for beta
}
inits
list(alpha=1, beta=25)
list(alpha=0.5, beta=75)
Notes: Again, be sure to stress checking for convergence.

## Slide 16: Results
Results for 100,000 samples (10,000 burn in)
Notes: This model takes a bit longer to converge. Illustrate this to the class.

## Slide 17: Results
Results for 100,000 samples (10,000 burn in)

## Slide 18: Empirical Bayes
Older approach but still used
Data are used to estimate parameters of first-stage prior
  Prior should not depend on observed data, so this is a criticism
  Does not directly include uncertainty in parameters
    Approximations can be used for this
  Prior then updated, with same data used to estimate prior
Can be viewed as approximation to hierarchical Bayes
Widely used in past analyses for NRC (e.g., NUREG/CR-6928)
Can be used to estimate initial values for hierarchical Bayes
Delivers parameters for each source
  Hierarchical Bayes requires a curve fit for individual sources

## Slide 19: Potential Issues with Hierarchical Bayes
Convergence can be a problem
  Especially when variability is not large
  Extremely diffuse gamma hyperprior for  can be a problem
    Try exp(1) hyperprior if there is a problem
  May need to reparameterize model to speed up convergence
Some results can be sensitive to choice of first-stage prior
  Especially when variability is very large
See (Kelly and Atwood, 2008) and BSEE PRA Guide, Appendix F, Population Variability Modeling (Vedros, 2017) for more details
Notes: Exp(1) is max entropy distribution for expected value of 1.

## Slide 20: Exercises
This example uses OpenBUGS to analyze a fairly large data set. The file “edg_data.txt” in the BUGS folder contains data for failure on demand for 195 EDGs. Recalling that the MLE of p is given by x/n, you should find that the MLE is > 0.05 for EDGs 183, 184, and 191-195.
There is a desire to demonstrate that Pr(p > 0.05) < 0.05. In English, we want to show that we are 95% sure that EDG reliability on demand is at least 95%. If we analyze each EDG separately, using a Jeffreys prior, we will find quite a few that do not meet the criterion (i.e., too many false positives).
Pooling the data would also be inappropriate, giving a very narrow credible interval for p; all of the EDGs would meet the criterion by a wide margin.
Notes: Use “hierarchical EDG FTS probability.odc” with initial values from that file. May want to discuss how to come up with different initial values. Make sure to check convergence. Should find that 95th percentile for EDGs 184, 193, and 195 is > 0.05.

## Slide 21: Exercises (cont.)
We would like to get a better answer than either of these simple approaches gives by developing a hierarchical Bayes model that describes the variation in p across the 195 EDGs in the dataset. As a starting point, use “hierarchical EDG FTS probability.odc” with initial values from that file but with the 195 EDG data points.
  Use OpenBUGS to analyze a hierarchical Bayes model for this data. Treat the number of failures for each EDG as binomial, with pi ~ beta(, ). Use independent diffuse hyperpriors for  and . We want to find which EDGs have Pr(p > 0.05) > 0.05.
  Re-analyze this model, using a uniform(0, 10) hyperprior for , and an independent uniform(0, 100) hyperprior for . Does this change in priors affect your conclusions about which EDGs have Pr(p > 0.05) > 0.05?
Notes: Use “hierarchical EDG FTS probability.odc” with initial values from that file. May want to discuss how to come up with different initial values. Make sure to check convergence. Should find that 95th percentile for EDGs 184, 193, and 195 is > 0.05.